[image: image10.png]Agilent EducatorsCorner.com Experiments
e ———————————————— —





[image: image10.png]​

Contact Bounce of a Relay

By: Walter Banzhaf

P.E. Professor of Engineering Technology

University of Hartford


Ward College of Technology
Abstract:

Electromechanical relays use an electromagnet to close or open electrical contacts. A common example of a relay is the starter relay an automobile engine. When the driver turns the key fully clockwise in the ignition/starter switch on the steering column, a small current (5 to 10 amps) is sent to a hefty starter relay. Sometimes this relay is an integral part of the starter motor, other times it is mounted elsewhere. You can always tell where the starter relay is, as there is a large diameter wire going from the battery + terminal to the starter relay.

When the small current flows through the relay's coil, a magnetic field is created which attracts a movable iron plate called an armature. The relay armature begins moving, and in a fraction of a second the electrical contact at the end of the armature touches a fixed contact, completing the electrical circuit between the battery and the starter motor. A rather large amount of current, typically 200 to 400 amps, flows into the starting motor and the engine begins to spin. In this way the starter relay remotely turns on the starter motor, reducing both the size of the wire running to the steering column and the cost and size of the steering column-mounted ignition/starter switch.

Equipment:

· Agilent 54600 - Series Oscilloscope 

· Agilent E3631A Power Supply

Circuit Explanation:

The relay coil is designed to operate on 12 VDC. Voltage is applied to the relay coil by closing the SPST switch connected to the supply voltage. The oscilloscope is triggered by the rise of voltage on Channel 1. Channel 2 shows the condition of the normally-open relay contacts: when Channel 2 is 0 V, the contacts are open, when it is +5 V, the contacts are closed. The quench diode across the coil prevents generation of a rather large voltage (due to Lenz's law) and arcing of the SPST switch contacts when the switch is opened.

[image: image1.png]+
12V

SPST

CH.

.|||-.

680




Figure 1

Measuring the time required for the relay contacts to open once the SPST switch is opened requires only that the triggering on Channel 1 be changed to negative slope.

Procedure A - Observing And Measuring Contact Closure Delay Time:
1)  Refer to the information in Figure 2 for oscilloscope control settings, and adjust your oscilloscope accordingly.

2)  Set the supply voltage to 12 V, and open the SPST switch. Press the RUN hardkey. Now close the switch. The sweep of the oscilloscope should be triggered once, and a new trace recorded (see Figure 2 for a typical display). You will have to press the Run hardkey after each trigger to "arm" the sweep again.

3)  Press the Stop hardkey, then press the Display hardkey followed by the Vectors On softkey. Vectors On essentially "connects the dots", giving a better display of the trace for Channel 2. Notable are the delay time between the application of the coil voltage and contact closure, and the many bounces of the contacts (lasting about 1ms) prior to their closing for good. In Figure 2, the contact closure delay is about 7.64 ms. Record the contact closure delay time in the table below.

4)  Change the supply voltage to 15 V, and then to 9 V, and repeat the measurement of delay time. Record results in the table. See Figures 3 and 4 for typical displays.

[image: image2.png]Supply Voltage (V)

Contact Closure Delay Time (ms)

9

12

15





Procedure B - Observing And Measuring Contact Opening Delay Time: 

1)  Keep the circuit and the probe locations as they were in procedure A. Return the supply voltage to 12 V. Change the oscilloscope settings as indicated in Figure 5.

2)  See Figure 5. Measure the time between opening of the SPST switch and the opening of the relay contacts, and record results in the table below. Notice the coil voltage dropping rather cleanly from 12 V to 0 V.

3)  Now, remove the quench diode, change the oscilloscope settings as indicated in Figure 6 (note the Ch. 1 V/Div!), and record the coil voltage and the load resistor voltage. A whole lot of shakin' is goin' on right after the switch opens! In Figure 6, the voltage on Ch. 1 is over 300 Vpp. Also notable is the contact bouncing, which did not occur when the quench diode was present.

CAUTION for Lab Manager: maximum voltage on scope is 400 V before damage. Be sure of values.

[image: image3.png]Quench Diode

Contact Opening Delay Time (ms)

In place across relay coil

Removed from relay coil





4)  In Figure 7, the time immediately after the switch opens is recorded. For about 200 ms, arcing occurs across the SPST switch contacts, resulting in high frequency oscillations with nearly 300 Vpp amplitude.

5)  Based on the above observations and data, can you explain why most electronic circuits involving relays with DC coils do use quench diodes?

6)  Why does the quench diode increase the contact opening delay time? What happens to the relay coil current at and after the time the SPST switch opens, with the diode present? with the diode absent?

[image: image4.png]1 5.00V 2 2.00V <0.00s 1.00%/ Sngl 41 sTOP

T
S ; i~ . . . (.
e e . L oLt e e e T e e e e .- - [, A D
Z Z = . . . (.
R i e R EEEE LR EEEEEEE A
Z I = . . . :Z Coil
e e o = = = e o = = =« e o o = = s.-.l-n ..... Voltage
I I = . . . r
H14~++-|-|--|-|-|-|-_--|-|-|-|---|-|-|-|---|-|-l-rrrHlfv-|-|-|-|-<11
. . I' . . . \ Load
___________: _____ : _____'_." _____ N L '_ ] Voltage
S | |
' ' - . 0 0 | 2
S A AR R, ‘1
. . - . . . [ B
. . - . . . ;e
t2 = 7.640ms At = 7.640ms 1/A = 130.9ms

State  Volts/Div Position Couplg BW Lim Invert Probe

Chan 1 On 5.000 V 156.3m V DC Off Off 10:1
Chan 2 On 2.000 V -5.937V DC Off Off 10:1
Chan 3  Off 100.0mV 0.000 V DC 1:1
Chan 4  Off 100.0mV 0.000 V DC 1:1
Main Main Time Delayed Delayed
Mode Time/Div Delay Ref Time/Div  Delay

Horizontal Normal 1.000ms/ 0.000s Left

Trigger Mode Source Level Holdoff Slope Couplg Reject NoiseRej
Single Ch1l 3.125V  200.0ns Pos DC Off Off

Display Mode: Normal
Cursors: t1=0.000s t2=7.640ms VI1(1)=0.000V  V2(1)=0.000V




Figure 2- 12 VDC Relay Contact Closure Delay Time, Supply Voltage = 12 VDC

[image: image5.png]1 5.00V 2 2.00V <0.00s 1.00%/ Sngl 4 1 STOP
y L} . . - I . . . .
| ' = [
..... b— : ek : : :
' ' ' e U ' ' .
. > |
.......... '..--..:.-...'-...-_::..-|.E.-...'-...-'...-.‘..-...
' ' ' - 1 ' B '
! - |
. —t I
. . . - | . . .
i . ' . : f ' . 1
Tt lIII-I- t144 -IIIIIIII:I-I-I'I‘*I*i-IIIIIIIII-I- 'I-III<:|T_
i ' . ' = .
----- '-----b----------l-----l--- r0-----!-----!-----.-----
i . . . = . . . .
! - I
""" """l’ '\""'l""';‘" I""""l""'l""'l’""'
] ' 0 ' o [ 0 ' .
e R : . U R e ?
| ' ' ' s [ 0 =
1 . . . = 0 . . .
tl = 0.000 s t2 = 4.760m At = 4.760ms 1/A = 210.1 Hz
State  Volts/Div Position Couplg BW Lim Invert Probe
Chan 1 On 5.000 V 156.3m V DC Off Off 10:1
Chan 2 On 2.000 V -5.937V DC Off Off 10:1
Chan 3 Off 100.0mV 0.000 V DC --- --- 1:1
Chan 4  Off 100.0mV 0.000 V DC - - 1:1
Main Main Time Delayed Delayed
Mode Time/Div Delay Ref Time/Div  Delay

Horizontal Normal 1.000ms/ 0.000s Left

Trigger Mode Source Level Holdoff Slope Couplg Reject NoiseRe;]
Single Ch1l 3.125V  200.0ns Pos DC Off Off

Display Mode: Normal
Cursors: t1=0.000s t2=4.760ms V1(1)=0.000V  V2(1)=0.000V




Figure 3 – 12 VDC Relay Contact Closure Delay Time, Supply Voltage = 15 VDC

[image: image6.png]2 2.00V <0.00s 2.007/ Sngl 41 sTop
N I I R R I B B P S oy S S R L B B YL oy S S -|-<11
""" T
) . . = . . . 2
--------------- T o e T -----------r----'<-|=
tl = 0.000 s t2 = 11.80ms At = 11.80ms 1/A = 84.75 Hz
State  Volts/Div Position Couplg BW Lim Invert Probe
Chan1l On 5.000 V 156.3m V DC Off Off 10:1
Chan2 On 2.000V -5.937V DC Off Off 10:1
Chan 3  Off 100.0mV 0.000 V DC --- --- 1:1
Chan 4  Off 100.0mV 0.000V DC - - 1:1
Main Main Time Delayed Delayed
Mode Time/Div Delay Ref Time/Div  Delay
Horizontal Normal 2.000ms/ 0.000s Left
Trigger Mode Source Level Holdoff Slope Couplg Reject NoiseRe;
Single Ch1l 3.1256V  200.0ns Pos DC Off Off
Display Mode: Normal
Cursors: t1=0.000s t2=11.80ms V1(1)=0.000V  V2(1)=0.000V




Figure 4 – 12 VDC Relay Contact Closure Delay Time, Supply Voltage = 9 VDC

[image: image7.png]1 5.00V 2 2.00V <0.00s 2.00%/ Sngl 41 sTOP

)

i
L} L} L} . l [} .
SRR RN NN A SRR R EEEE NS ST S R EEEE
- : . - L r . -
]

a2

tl = 0.000 s t2 = 10.72ms At = 10.72ms 1/At= 93.28 Hz

State  Volts/Div Position Couplg BW Lim Invert Probe

Chan 1 On 5.000 V 0.000 V DC Off Off 10:1
Chan2 On 2.000 V -5.937V DC Off Off 10:1
Chan 3  Off 100.0mV 0.000 V DC - - 1:1
Chan 4  Off 100.0mV 0.000 V DC - - 1:1
Main Main Time Delayed Delayed
Mode Time/Div Delay Ref Time/Div  Delay

Horizontal Normal 2.000ms/ 0.000s Left

Trigger Mode Source Level Holdoff Slope Couplg Reject NoiseRe]j
Single Chl 7.187V  200.0ns Neg DC Off Off

Display Mode: Normal
Cursors: t1=0.000s t2=10.72ms VI1(1)=0.000V  V2(1)=0.000V




Figure 5 – 12 VDC Relay Contact Opening Delay Time, Quench Diode Present Across Relay Coil

[image: image8.png]% 50.0V 2 2.00V <0.00s 5004/ Sngl L1 STOP
y : ) ) [ . . ) )
| ' . = . .
---------------- S s A
: : C ; ; . : .
""""" T T T T T T T e —————— ’ al
) Z - . . ' Z N
.......... 1 A
: Z - . . . Z
' ! e . . !
R R R e T R R NN T AR
M e e cegeeees T R
___________ T — . . P
tl = 0.000 s t2 = 1.960ms At = 1.960ms 1/A = 510.2 Hz
State  Volts/Div Position Couplg BW Lim Invert Probe
Chanl On 50.00 V 100.0 V DC On Off 10:1
Chan2 On 2.000V -5.937V DC Off Off 10:1
Chan 3  Off 100.0mV 0.000 V DC -—- - 1:1
Chan 4  Off 100.0mV 0.000 V DC - --- 1:1
Main Main Time Delayed Delayed
Mode Time/Div Delay Ref Time/Div  Delay

Horizontal Normal

Trigger Mode Source Level
-148.4V

Single Ch1
Display Mode: Normal

Cursors: t1=0.000s t2=1.960ms

500.0us/ 0.000 s

V1(1)=0.000 V

Left

Holdoff Slope Couplg
200.0ns

Neg DC

Reject NoiseRe;
Off Off

V2(1)=0.000 V




Figure 6 – 12 VDC Relay Contact Opening Delay Time, Quench Diode Absent Across Relay Coil

[image: image9.png])

i
tl = 0.000 s t2 = 200.0us At = 200.0us 1/A = 5.000 kHz
State  Volts/Div Position Couplg BW Lim Invert Probe
Chan 1 On 50.00 V 100.0 V DC On Off 10:1
Chan 2  Off 2.000V -5.937V DC Off off 10:1
Chan 3  Off 100.0mV 0.000 V DC - --- 1:1
Chan 4  Off 100.0mV 0.000 V DC - --- 1:1
Main Main Time Delayed Delayed
Mode Time/Div Delay Ref Time/Div  Delay

Horizontal Normal 50.00us/ 0.000s Left

Trigger Mode Source Level Holdoff Slope Couplg Reject NoiseRej
Single Ch1l -181.3V 200.0ns Neg DC Off Off

Display Mode: Normal
Cursors: t1=0.000s t2=200.0us VI1(1)=0.000V  V2(1)=0.000V




Figure 7 – Coil Voltage of 12 VDC Relay Being Turned Off, Quench Diode Absent Across Relay Coil

� EMBED Word.Picture.8  ���








[image: image11.wmf]


_1030875879.doc
[image: image1.png]Agilent Technologies
EducatorsCorner.com Experiments








